## Server room details
A | DOUBLE CONVERSION TRUE ON-LINE UPS
SL. | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL PRICE
1 | Brand - Model - Origin - Europe Standard - Un-interrupted Power Supply System that will work in Parallel redundant mode. The UPS system will supply clean continuous power to the Server Room with SNMP / BMS agent and 1x Ethernet port. SNMP Agent software for Windows and for Linux for the use of management of the UPS system - All Fittings with the necessary power cables and installation kits for all UPS wiring - Imported battery cabinet made with Imported MS angle bar by the UPS manufacturer. Technology - VFI, double conversion with integrated transformer Capacity - 20 KVA True Online Transfer Time - zero Backup Time: 60 minute in full load Wave Shape - Pure Sine Wave Battery Type - Maintenance-free Sealed Lead acid Input Voltage - 320 ~ 460/184 ~ 265 VAC, 3 Phase/single phase Output Voltage - 415/240 V ±1%, 3 Phase (User selectable) Input Power Factor - 0.98 Output Frequency - 50/60 Hz, +/- 0.05 %( User selectable) Output Power Factor - 0.9 Phase - Three–Three+ Neutral and Earthing Inverter - SVM (Space Vector Modulation) or PWM and IGBT technology Noise Level - 55 dB
2 | Microprocessor based monitoring and control system Computer Interface - Support RS 232 for UPS monitoring software High Availability - LCD and Mimic Panel, RS232 port, auto battery test, volt free contacts, SNMP Installed, Intelligent Energy Management, Maintenance By-pass, etc. Storage battery - High performance sealed battery with 3-5 years design life and 3 years warranty. Warranty - 3 years full warranty with parts and onsite service & labor3
3 | Installation Testing & Commissioning Charge |  | 2
Sub-Total Taka for A:
B | PRECISION AIR CONDITIONER
Sl. | Description | Unit | QTY | UNIT PRICE | TOTAL PRICE
1 | Precession Air Condition (PAC) Dunham-Bush Down Flow Type Brand Model Origin - Europe Standard - a) The Server Room to be maintained at a set temperature between 20 and 22 degrees Celsius 24 hours a day, 7 days a week and it is user selectable. b) The Server Room to have a constant humidity level of 50 percent, plus or minus 10 percent (45 percent to 55 percent). Capacity - 18.8KW minimum Sensible Heat Factor = 0.9 Air Distribution - Down flow with Top Return Air Compressor + Supply Fan Input Power Auto restart after power outage Warranty 3 year full warranty with onsite parts, service and labour PAC Mode of Operation: There are (1 +1) PACs (Precision Air Condition Unit) down flow type to maintain the environment in the Control Center with total area of 464 sft. There should be redundancy in the case of any failure in one of the PAC. Please specify the following components /functionalities to ensure quality of the PAC unit in the bid: Cabinet Cooling Coil Fans Electric Heaters Filtration Compressor and Safety Controls | No. | 2
2 | Dehumidification Electric Panel Microprocessor Controls Base Stand Horizontal Discharge Section Filter Gauge Double Skin Panels Water Detection VRF System Condenser Fan Pressu+ B5re Switch Screwed Water Connections Hand/Off/Auto Interface Auxiliary I/O Interface Step Controller Interface Emergency Power Off System
3 | CONTROL : Microprocessor Based automatic Temperature, Humidity and Filtration Control Controller Feature: * Unit ON/OFF key, providing “master” control of the local unit. * Graphical liquid crystal display, providing icon status of the unit functions, parameter menus, Trend logging, alarm buffer and access to other controllers via the network system. * Programmable keys, providing access to large graphical/ local network display featuring various functionalities such as manual key operation for silencing the local audible alarm, Access to Millennium Access Module configuration menu. Alarm Monitoring Display (via Millennium Access Module) comprises: * ON/OFF key providing “power on” to graphical display. * Graphical liquid crystal display, providing alarm status from networked. * Four programming keys, providing access to alarm buffer. * Mute key for silencing the local and remote audible alarms.
* Please specify the steel cage and installation of external unit also.
4 | Installation Material, Testing & Commissioning Charge |  | 1
Sub-total for B:
C | SPLIT TYPE AIR CONDITIONER FOR POWER & NOC ROOM
Sl. | Description | Unit | QTY | UNIT PRICE | TOTAL PRICE
1 | Split Type Air- Conditioner. Wall mounted with wireless remote control & clock, Capacity 1800BTU/h. 1.5-Ton | No. | As per design
2 | Automatic Controller | No. | As per design
3 | Installation Material, Testing & Commissioning Charge | No. | 1
Sub-total for C:
D | INTERIOR DECORATION WITH CIVIL WORKS
SL. | DESCRIPTION | UNIT | QTY. | UNIT PRICE | TOTAL PRICE
1 | Dismantling works: Dismantling of the existing 10"/5" bricks wall/existing chamber as per drawing-design and stack the debris to the safe distance as per instruction. | Sft. | As required
2 | Aluminum Partition Work: Supplying fitting and fixing of aluminum portion of protector bit' anodized ‘Silver’ color aluminum section with 10 mm clear glass all foreign made hardware of best quality available viz; original bronze anodized star head matching, screw, weather seal & approved quality complete in al respect as per design, drawing and direction of Architect. | Sft. | As required
3 | Brick Works: 10" brick work with both side net finishing, 1st class bricks in cement morter(1:4) and making bond with connected walls in/c racking out joints, filling the intersects with morter, cleaning and soaking the bricks at least for 24 hours before use and washing of sand, necessary scafolding, curing at least 7 days. all complete as per direction. | Sft. | As required
4 | Plaster Works: Minimum 1/2" plaster to wall(1:6) inner sarface of the building, finishing the corner and edges in/c removing the existing damp plaster (if necessary), washing of sand ,cleaning the surface with clean water,necessary scafolding, curing at least 7 days. all complete as per direction. | Sft. | As required
5 | Frosted Paper: Supplying fitting and fixing self adhesive frosted paper (4'-6") on door and glass panel door surface after lettering with fine finish etc complete as per direction of Architect. | Sft. | As required
6 | HALF HEIGHT FABRIC PARTITION: supplying fitting & fixing of partition 2" thick & 4'-0" high made of ply wood frame with fabric covered both side and top with aluminum extension mid and lower portion of the panel have cable passing management, upper portion all complete & full satisfaction of authorty. | Sft. | As required
7 | WORKSTATION TABLE: Supplying, fitting & fixing at site (1200mm X 600mm) made of 25mm thick laminated particle-boards table top having both sides laminated pasted & fittings in half height system partitions with clumps, keyboard tray & drawer units made of 18mm thick laminated board with pasted PVC edging having three drawers with locking arrangment etc. All complete as per design. | Unit | 4
8 | EXECUTIVE CHAIR: Supplying at site imported chair,with intimate contact lumber-support medium-high tilting-back seats with hydraulic lift upon base on 5 castor wheels etc. All complete and approved colour and quality including under materials. | Unit | 6
9 | PVC FLOOR MAT FOR ENTRY: Supply, fitting & fixing of imported best quality PVC Floor Mate of approved colour,cutting with fine finish etc. | Sft. | As required
10 | SIGNAGE: Supply, fitting & fixing of sinage for NOC, Store & Fire room, Server Room area and UPS & Power room made by plastic wood & sticker at front side of all room as per direction. | Sets | 3
11 | Ceiling Mounted Energy Saving Light: PL LIGHT SET. (220/240V-195mA), Single Phase 23~25 Watt, 50~60 Hz. Supply, fitting and fixing ceiling mounted fixed 6",Energy Saving light set Decorated shade and all other accessories as per drawing and specification. Specify brand, origin. | Nos. | 20
12 | Silver color Aluminium Channel for Lighting Wiring through Horizontal fixing ceiling mount with royal plug, screw and other accessories | Mtr. | As required
13 | Roof Painting at the server room | Sft. | As required
14 | Tempered Glass Door 3.5 ft | Nos. | 2
15 | Tempered Glass Door 3 ft | Nos. | 3
16 | Mild Steel Collapsible Door | Nos. | 1
17 | Wall Painting at the Server Room | Sft. | As required
18 | Water /damp /moist /leakage prevention from the roof and sidewalls | Sft. | As required
19 | Installation Material, Testing & Commissioning Charge |  | 1
Sub-Total Taka for D:
E | ELECTRICAL WIRING
SL. | Material Name | Unit | Qty. | UNIT PRICE | TOTAL PRICE
Distribution Box
1 | Main Distribution Box - 16SWG Sheet Steel Including Busbar(500Amps), Insulator,Internal Ebonite Cober for Busbar Section,Ammeter-01 no,Voltmeter-01 no,Selector Switch-02 nos, Current Transformar-03 nos,Indication Lamp-03 nos, Lock with Powder Coated Paint Finished. | Nos. | 1
2 | Sub Distribution Box for UPS In Out: 16SWG Sheet Steel Including Busbar(300Amps), Insulator,Internal Ebonite Cober for Busbar Section,Ammeter-01 no,Voltmeter-01 no,Selector Switch-02 nos,Indication Lamp-03 nos, Lock with Powder Coated Paint Finished. Origin: | Nos. | 2
3 | Sub Distribution Box for PAC And Others: 16SWG Sheet Steel Including Busbar(300Amps), Insulator,Internal Ebonite Cober for Busbar Section,Ammeter-01 no,Voltmeter-01 no,Selector Switch-02 nos,Indication Lamp-03 nos, Lock with Powder Coated Paint Finished. | Nos. | 1
Electrical Cabling
All electrical cabling /wiring components should be ISO 9002:1994 and ISO 9001:2000 certified as specified by the Eastern Cables Limited, Bangladesh Steel and Engineering Corporation (BSEC), Ministry of Industries, Government of Bangladesh.
4 | Cable for MDB Input Output (A-87)-NYY-4x35RM , Main Cable: PVC sheeted 4 core cable rated voltage 600/1000V,Permissible Voltage 720/1200 Fixed: -40°C to +70°C for cable through under ground by PVC/GI pipe for LT Panel to DATA Centre MDB wiring at IT floor (2nd floor) which low copper loss and BSTI approved. including 10re single core earthing line. | Raft. | As required
5 | Cable UPS Input Out Put (A-90)-NYY-1x35RM: PVC sheeted 4 core cable rated voltage 600/1000V,Permissible Voltage 720/1200 Fixed: -40°C to +70°C for cable through trunking channel for DATA Centre MDB to UPS (1&2) input and output wiring at IT floor (2nd floor) which low copper loss and BSTI approved. including 6re single core earthing line. | Rft. | As required
6 | Cable For PAC (A-94)-NYY-1x10RM or 4x4RM: PVC insulated PVC sheeted 1 or 4 core cable (depending on the phase of PAC) rated voltage 600/1000V,Permissible Voltage 720/1200 Fixed: -40°C to +70°C for cable through trunking channel for DATA Centre MDB to Precision Aircon (1&2) wiring at IT floor (2nd floor) which low copper loss and BSTI approved. including 2.5re single core earthing line. | Rft. | As required
7 | End Level Distribution Cable BYA 3x6rm or NYY1x6 rm PVC insulated PVC sheated Dual core cable (Red & Black) rated voltage 550/750V,Permissible Voltage 350/450 Fixed: -40 to +70°C for cable through trunking channel from SDB-1&2 to each Server Rack to be ensured Phase,Neutral & Earthing for Industrial Socket wiring at Power room to Data Centre, IT floor (12th floor) which low copper loss and BSTI approved.including 2.5re earthling cable. | Rft. | As required
8 | Cable For Light BYA - 2.5RM BYFY PVC insulated PVC sheated Dual core cable (Red & Black) rated voltage 550/750V,Permissible Voltage 350/450 Fixed: -40 to +70°C for cable through Cable Ladder from SDB-1&2 to each Server Rack to be ensured Phase,Neutral & Earthing for Auxiliary Socket wiring at Power room to Data Centre, IT floor (12th floor) which low copper loss and BSTI approved.including 1.5re earthling cable. | Rft. | As required
9 | Circuit Breaker
10 | MDB Input Output (MCCB-125A)(TP) - Tripple Pole Adjustable Trip Current Moulded Case Circuit Breaker for Main Incoming Breaker of Server Room. Origin: Europe. | Nos. | 1
11 | UPS Input Output (MCCB-125A) - Single or Tripple Phase (please proposed) Pole Adjustable Trip Current Moulded Case Circuit Breaker for incoming breaker of UPSes. Origin: Europe. | Nos. | 4
12 | PAC Output (MCB-40A) - Single or Tripple Pole Adjustable Trip Current Moulded Case Circuit Breaker for PAC - 1&2 Input and Ouyput Breaker. Origin: Europe. | Nos. | 2
13 | MCB for Industrial Socket (DP-32A) - Single Pole Adjustable Trip Current Miniature Circuit Breaker for Industrial Socket. Origin: Europe. | Unit | As required
14 | MCB for MK Socket (DP-20/16A) - Single Pole Adjustable Trip Current Miniature Circuit Breaker for Auxiliary Socket. Origin: Europe. | Unit | As required
15 | MCB for Down Light or Fire Units or Other points (DP-16/10A) - Single Pole Adjustable Trip Current Miniature Circuit Breaker for said purpose. Origin: Europe. | Unit | As required
16 | Electrical Accessories
17 | Cupper Bus bar | Kg. | 5
18 | Industrial Socket: 3-Pin socket with earthling point , 220v~250v AC, Maximum Current 40Amps Operating Temperature: <-5ºc~55ºc>,with protected cover and gripper. Origin: Europe | Unit | As required
19 | MK Socket: AUXILIARY SOCKET: 3-Pin socket with earthling point , 220v~250v AC, Maximum Current 16Amps Operating Temperature: <-5ºc~55ºc>,made of fire proof materials with PVC MK box. Origin: Europe. | Unit | As required
20 | Trunking Chanel / Cable Ladder / Flexible Pipe
21 | Trunking Channel For Power (5"X3") | Unit | As required
22 | Overhead Thai Channel For Light and Fire (3"X1.5") | Unit | As required
23 | Light Shades, Supporter, Latch, Tie & Others Accessories | Unit | As required
24 | Flexible Pipe For Electrical Wiring | Unit | As required
25 | Electrical Tape Tie and Others | Unit | As required
26 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for E:
F | Grounding /Earthing System
SL. | Material Name | Unit | Qty. | UNIT PRICE | TOTAL PRICE
1 | Copper Wire (Size: SWG8) | mtr | 45
2 | Copper Rod | mtr | 2
3 | G.I. Pipe (1.5”) diameter | mtr | 45
4 | From the ground to Equipment room through PVC pipe:
5 | Cable Size 10 rm BYA ( Green Insulation) | mtr | As required
6 | PVC pipe: ¾ inch diameter | mtr | As required
7 | Saddle: ¾ inch | Unit | As required
8 | Royal Plug |  | As required
9 | Wooden Screw |  | As required
10 | Copper Bar & Clamp 12inch X 1.25inch X 3mm bar with clamp | Unit | As required
11 | G.N.D Bus-bar (Long) | Unit | 1
12 | G.N.D Bus-bar (Small) | Unit | 1
13 | Cable 2.5re | mtr | As required
14 | Cable Lux | Unit | As required
15 | Other Accessories | lot | 1
* The grounding material should have adequate electrical properties to achieve the resistance of < 2 Ohms * Grounding should be inserted from 2 (two) different points separated at least by their length and connected to a common bus bar
16 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for F:
G | Rack Cabinet for Network Equipments
SL. | ITEM / DESCRIPTION | Unit | QTY | UNIT PRICE | TOTAL PRICE
1 | 42u 19" Rack 600mmX 900mm depth closed rack comes with frame top cover, 2 pcs side panels, 1 pc front glass door, 1pc rear door, 2 pcs 5 way power strip, 1 pc equipment shelf, 4 pcs caster wheel with adjustable feet, cagenut & screw, standard color frame Sony Blue with Black panels. Origin: USA (Please specify brand and origin) | No. | 1
2 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for G:
H | Raised Flooring System
SL. | ITEM / DESCRIPTION | Unit | QTY | UNIT PRICE | TOTAL PRICE
1 | Floor Panel Surface Finish: The floor Panel is consist of a high density Particle Board.V313 moist Resistant quality.Which is extremly durable, wear resistant and easy to Clean. Difficult stains. The Laminate is also resistant to harsh acids and chemicals.The Laminate is direct Laminated, Therefore no glue.
Ventilated Floor Panel: The floor Panel is consist of a high density Particle Board.V313 moist Resistant quality.Which is extremly durable, wear resistant and easy to Clean. Difficult stains. The Laminate is also resistant to harsh acids and chemicals.The Laminate is direct Laminated, Therefore no glue.
Pedstal: Should offer great flexibility for electrical power room, Server Room etc. This is buildup around a perfabricated steel framework,whichis bolted together.It consists of tubularsections measuring 80X40X1.5mm. The structural pedstal supports made from the same section can be adjusts +/-50mm from the nominal floor height.
Loading Criteria: The flexible and adaptable Iso floor construction allows for unform distributed loads UDL between 8kN/sqm
Material: HD Particle Board. V313 moist resistant
Diamentions: 600X600X38mm
Surface finish: Laminated as standard
Space under Raised floor: 24 inch clearance under the floor of ± 4 inch Adjustable Pedstal
Colour Pattern: M335 Granite as standard
Electrical Resistant: >500 KΩ and <400.000MΩ
Wear resistance: 4000-6000 cycles according to EN 438-2:6 1991
Weight: 10 kg (22 lbs) per panel
2 | Foil Paper | Sft. | As required
3 | Panel Lifter | Nos. | 2
4 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for H:
I | Network Cables
- All network cables used should be Systimax /Panduit with all structured cabling standards properly maintained - Manufacturer's Authorization Certificate should be provided
SL. | ITEM / DESCRIPTION | Unit | QTY | UNIT PRICE | TOTAL PRICE
1 | Patch Panel CAT6-24 Port | No. | As required
2 | Network Cable CAT6 | Box | As required
3 | 1m CAT-6 Patch Cord. | No. | As required
4 | Face Plate Double Face Plate,CAT6 Module | No. | As required
5 | Modular Jack | No. | As required
6 | Horizontal Wire Manager | No. | As required
7 | Cable Conduit | lot | As required
10 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for I:
J | FIRE SUPPRESSION SYSTEM
SL. | Description | Unit | Qty. | UNIT PRICE | TOTAL PRICE
SUPPRESSION SYSTEM
1 | Feature of Fire Suppression System: - Standards and codes of practice applicable should be mentioned. - Should UL or NFPA certified. The following design data shall be submitted at the bidding stage as a minimum requirement:- * Mass of fire suppression agent composition used and design concentration. * Quantity and model of the fire suppression agent canisters. * Mounting and installation method. * Proposed fire detection, indication and control method. | Nos.
2 | Hazard to Environment The fire suppression agent shall have Zero Global Warming Potential index and Zero Ozone Depletion Potential index. It shall be listed under the U.S. Environmental Protection Agency’s (EPA) Significant New Alternative Policy (SNAP) program as an acceptable alternative to Halon. Design Concentration The Fire Suppression System used is intended to suppress Class A and Class B fires. The design concentration of the fire suppression agent shall be stated clearly. Test results by an independent and internationally recognized Authority on the effectiveness of the agent at the design concentration in suppressing Class A and B fires shall be submitted during bidding stage. After sales Service and Guarantee The Principal (or authorized agents) of the system shall have agents at the regional level in Bangladesh and inventory shall be available locally to facilitate prompt replacement when required. The bidder must guarantee the performance of the system for a period of 36 months upon completion of installation. Modes of Operation a) Automatic Operation b) Any failure of the control panel shall not affect the automatic discharge capability of the system.
3 | Activation of any single detector in any detection zone shall:- a) ause the first stage alarm b) Illuminate the lamp on the activated detector c) Illuminate a lamp on the Fire Control Panel (FCP) d) “Evacuate Area Immediately” sign activates and strobes e) Transmit ALARM signal to Indication Panel Activation of a thermal detector on the discharge loop shall:- a) Cause a second stage alarm – strobe and sounder activates. b) Operate auxiliary contacts to trip the electrical power supply to the protected area including power to the AHU. Power to essential services i.e. emergency circuits, fire and security panels, etc. shall NOT be affected. c) Initiate immediate discharge of the fire suppression components. d) Transmit DISCHARGE signal to Indication Panel. Manual Operation Shall be performed electrically by a dual action Manual Release point placed directly at the entrance to the protected area. Activation of the Manual Release point shall initiate immediate discharge of the fire suppression system components.
4 | General Detection and Control Systems shall be used in accordance to NFPA 72E (Standard on Automatic Fire Detectors). The system shall be designed such that automatic actuation occurs only upon activation of two detectors within the same area. Adequate and reliable primary and 24 hours battery back-up shall be provided to ensure continued operation of the signaling, and control requirements of the system. Operating Alarms and Indicators Alarms and indicators shall be used to indicate the operation of the system, fire hazards, or failure to any supervised device. Failure indication shall be separate and distinct from alarm indicating operation or hazardous condition. Control Panel The control panel shall be built to comply to IP54, in a non-combustible cabinet of sheet steel with hinged lockable front doors. The panel shall incorporate the following features:- Indicator lamps for: “AC ON”, “CHARGER ON”, “AC FAIL”, “CHARGER FAIL”, “BATTERY FAIL”, “NORMAL” and “TROUBLE” fire conditions. Switches for SYSTEM RESET & BATTERY TEST DISCHARGE indication Audible FAULT buzzer with SILENCE switch
5 | BELL SILENCE switch Ammeter and Voltmeter for battery Labels Chargers for the supplied maintenance-free sealed lead acid battery Control Panels should be accompanied by a test report from the supplier/manufacturer and certified to meet performance requirements indicated for the installation.
6 | Installation Material, Testing & Commissioning Charge | Nos. | 1
Sub-Total for J:
K | DIGITAL CCTV SYSTEM
SL. | Description | Unit | Qty | UNIT PRICE | TOTAL PRICE
1 | Digital Video Recorder, 8 Channel with 320 GB HDD C/W VGA Adapter for 30days recording report facilities. | Nos. | 1
2 | Fixed Dome Camera (Night vision) | Nos. | 6
3 | Site Monitoring Software - Up to 16 site\DVR Server one at a time connection, Receives alarm from DVR Server | Nos. | 1
4 | 19” LCD Color Monitor (Brand should be same as servers) | Nos. | 1
5 | Cabling c/w PVC conduit for RG-6 coaxial /1.5 rm /RJ 58/59 cable | mtr | As required
6 | Power Cable | rm | As required
7 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for K:
L | Intelligent /Static Transfer Switch
SL. | Description | Unit | Qty. | UNIT PRICE | TOTAL PRICE
1 | Nominal rating - 16 A Single phase voltage with neutral - 220 V / 230 V / 240V Input source - 2 Output - 1 (having 4-5 sockets) Admitted voltage variation on the input - +/-15 % (settable up to +/-10 +/-20%), Frequency - 50 Hz or 60 Hz, Overload capacity - 1 min 200%, 30 min 125 % , Admissible crest factor - up to 4 Transfer time < 3 ms (should be un-interrupted) | Nos | 1
2 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for L:
M | TVSS SYSTEM
SL. | Description | Unit | Qty. | UNIT PRICE | TOTAL PRICE
1 | Country of origin - UK/USA/any EC Country | Unit | 1
Electrical Characteristics -
Nominal Operating Voltage - Vn - 277V ± 3%
Maximum Continuous Operating Voltage - 350V ± 3%
Vref (peak) @ 5mAmp AC (peak) - 607V ± 3%
Vref @ 5mAmp DC - 582V ± 3%
Operating Frequency Range - 25…500Hz
Leakage Current at Vn - 0..90mA
Surge Protection Levels -
Suppressed Voltage Rating (SVR) - 900V ± 3%
Response Time - <5 ns
Maximum Surge Current -
Maximum Surge Current - Imax (8/20) NEMA LS-1 - <as mentioned below>
Maximum Lightning Current - Iamp (10/350) IEC 61643-1 -
Let Through Voltage Level -
for surge current 10kA* (8/20) (IEEE C62.41-1) - 930V
Long Duration Surge Performance -
1kA square waveform 2msec (IEEE C62.11) -
500A square waveform 2msec (IEEE C62.11) - 250hits
Direct (in-line) Installation Guidelines - TVSS modules should be tested for safe installation behind:
- * 1600A time delay fuse at available fault current 200kA
- * 200A breaker at available fault current 100kA
- * 400A breaker at available fault current 38kA
Surge Counter - Should be available
Environmental Properties -
Operating Temperature (degree C) - -40…+85
Environmental Protection - IP65
Mechanical Properties -
Diameter inch (cm) - <specify>
Height inch (cm) - <specify>
Weight lb (gr) - <specify>
Standards Compliance -
IEEE C62.41 - IEEE C62.45 - IEEE C62.11 - NEMA LS-1 - IEC 61643-1 - IEC 61643-12 -
2 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub-total for M:
N | ENVIRONMENT MONITORING SYSTEM
SL. | DESCRIPTION | Unit | QTY | UNIT PRICE | TOTAL PRICE
1 | The Server Environment Monitoring System monitors critical environmental conditions, such as temperature, humidity liquid presence, motion, intrusion, and vibration. When a sensor exceeds a configurable threshold, the system will notify us via email, LEDs, alarm beacon, web page, network management (SNMP), and SMS messages (via external GSM modem). | Unit | 1
The system includes three internal sensors: temperature, humidity and power. It should also supports 16 external configurable sensors and eight digital input sensors. The system should have the following capabilities:
* Monitor and manage server room environmental and security conditions over IP. * Create alarm signals with customized input parameters. * Four output relays for control of external devices. * Relays activate upon alarm or via the user interface. * Supports IP network video camera. * Live view of a facility from anywhere, anytime. * Monitor (ping) up to 64 IP network devices. * Alerts are sent if devices are not responding. * Provides power supply for all sensors. * Internal battery backup. * 1RU rack mount case is standard. * Up to four units can be used together to increase the number of sensors connected. * Connect the units using CAT5 expansion cables or via Ethernet interface. * Uses a single Web interface for all systems connected.
Technical Specification 1. Power Port 2. RJ45 Sensor Ports – around 16 RJ45 modular jacks for connecting NTI temperature, humidity, temperature/humidity, liquid detection, smoke detection, glass break, vibration and motion sensors. 3. Digital Inputs 4. Output Relays 5. Beacon Port 6. Siren Port 7. Expansion Ports 8. Console Port - 1 female DBS RS232 serial port for terminal access. 9. AUX Port - 1 male DB9 RS232 serial port for controlling and monitoring external equipment, such as GSM modem. 10. AUX Power Port 11. Ethernet Port 12. Internal Temperature Sensor 13. Internal Humidity Sensor 14. Internal Power Sensor 15. Back-up Battery 16. Environmental: a. Operating temperature: 32°F to 100°F (0°C to 38°C). b. Storage temperature: -22°F to 140°F (-30°C to 60°C).
2 | Space Temperature and Humidity Sensor
4 | Liquid Detection Sensor For warning of flooding; Detects liquid depth >0.1"; Minimum puddle: 0.6" diameter; 100% waterproof electronics; Detects any liquid, except demonized water. | Unit | 4
5 | RJ45 connector Supports CAT5/5e/6 cable up to 1,000 ft. (not included) | Unit | As required
6 | Door Contact Sensor Monitors access with a magnetic bridge sensor, which responds to any magnetic material (no special inserts necessary). | Unit | 2
7 | Glass Break Detection Sensor a. Acoustically detects the cracking of glass. b. Adjustable sensitivity. | Unit | 1
8 | Shock and Vibration Sensor | Unit | 3
9 | Water Leak Detection Cable | mtr | 10
10 | Cabling c\w PVC Conduit for Environment Monitoring System (power and network - please specify the type and details) | rft | As required
11 | GSM Modem with SIM card and credit charged for 3 years required for SMS Alerts | Unit | 1
12 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub total for N:
O | ACCESS CONTROL
SL. | Description | UNIT | QTY | UNIT PRICE | TOTAL PRICE
1 | Access Controller (for IN and EXIT)
| Model - Manufacturer - Country of Origin - Malaysia Clock - Real Time Clock with lithium battery back up Device type - Control interface c/w reader Controller finger template - 2000 Card Users - "10 - 000" Transactions - "10 - 000" In Reader - Built In Out Reader - External Output - 1 EM Lock Input - Door Sensor and Push Button Additional I\O - 4 input and 6 output Buzzer - Built In Tamper Switch - Built In Modes of Operation - "Finger Only - Card + Finger - Card + PIN - Card only" Built in card reader - Mifare Smart Card Reader (Weigand format) Scanner Type - Silicon fingerprint scanner at least 500dpi Enrolment - 2 finger per user False Rejection Rate - 0.5% or better False Acceptance Rate - 0.01% or better Verification Time - <1 sec Display - 2 X 16 Characters backlit LCD Identification - One-To-Many (1:N) & One-To-One (1:1) Keypad - 16-key keypad Holidays - Minimum 35 Timezone - Minimum 20 Timer - Minimum 20 Baude rate - 2400 to 57600 Communication Interface - "RS485 (Biometric to Biometric) - TCP/IP LAN (optional)" | Nos | As per proposed design layout
Radio Frequency - 13.56 Mhz Communication Output - Wiegand/40 Bit Free Wiegand Adjustable Lock release time - Available Permanent Lock release - Available Inhibit access - Available Continuous swipe - Available Anti passback - Available Automatic lock release time zone - Available Automatic Pin\Finger print disable time zone - Available Operating Temperature - -15oC to 60oC Humidity - <85% non-condensing Power Requirements - 12V/1000mA Dimensions - "8""X6""" Approximate Weight - 600gram Data Format - Weigand 26-40 bits Card Reading Range - 3-5 cm
2 | Electro magnetic Lock Model - Manufacturer - Country of Origin - Malaysia Lock Type - Electromagnetic Lock Power DC - 12 Volt Operating Current - 601 mA Temperature - 10oC to 60oC Holding Force - At least 600 lbs Delay Time - Specified by controller Door Swing angle - 90o | Nos | As per proposed design layout
3 | Mifare Contact less Smart Card Model - Manufacturer - Country of Origin - Malaysia Internal Memory 4 Kilo Byte (For card access and finger print storage and other applications) Protocol - 26\32 bit wiegand Format Dimensions - 85.6 x 53.98 x 0.8 mm Color - Plain white Material Material - PVC Lamination | Nos | 10
4 | Power supply unit (c/w 12 Vdc, 7 AH battery back up Switch Mode Power Supply Unit. 220-240 V AC) | Nos | As per proposed design layout
5 | Windows-based Door Access Control Management System Software - 16 Doors | Nos | As per proposed design layout
6 | ZL Bracket / U Channel | Nos | As per proposed design layout
7 | Emergency Lock Release Key | Nos | As per proposed design layout
8 | Cabling with conduit and fittings (CAT 6, 3, Core Power Cable) | Lot | 1
9 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub total for O:
P | Additional Accessories
SL. | Description | UNIT | QTY | UNIT PRICE | TOTAL PRICE
1 | Aluminum self supporting platform ladder (5 Step) | Nos | 1
2 | Fluke 87-5 Digital Multimeter with Fluke Meter Case | Nos | 1
3 | Wet And Dry Vacuum Cleaner - 1500W - 25l container - Wet and dry filter cartridge | Nos | 1
4 | Imation Disc Stakka Storage CD/DVD automated carousel | Nos | 1
5 | Rechargeable torch light with replacement batteries. | Nos | 1
6 | Installation Material, Testing & Commissioning Charge | Job | 1
Sub total for P: